## Start Here
THE FRP TANK INSPECTION FIELD WORKBOOK
Inspection planning, condition documentation, and a 99-condition visual reference for facility engineers and maintenance teams.
HOW TO USE THIS WORKBOOK |  |  |  | LIVE RECORD SUMMARY
01 | Prepare | Complete tank data and gather drawings, service history, prior reports, and repair records. |  | Metric | Current value | Metric | Current value
02 | Coordinate | Review the inspection objective, access, operating state, facility controls, and required personnel. |  | Observed conditions | 0 | Observation records | 50
03 | Observe | Follow a consistent route and record location, extent, surface state, photograph IDs, and comparison. |  | Prompt evaluations | 0 | Emergency procedures | 0
04 | Reference | Use the 99-condition atlas to improve terminology and prepare questions - never as a diagnosis. |  | Photo log entries | 40 | Work orders opened | 0
05 | Handoff | Summarize observations and route follow-up through facility procedures and qualified evaluation.
EDUCATIONAL LIMITATION This workbook supports inspection planning and documentation. It does not diagnose damage, determine fitness for service, authorize confined-space entry, define a repair, or replace manufacturer instructions, facility procedures, applicable requirements, or qualified professional judgment. Educational illustrations may not match every field condition.
PLASTECH CONTACT AND SERVICE PATHS
Contact | Value | Open | Use when
Phone | (410) 737-4700 | Call | Call Plastech
Website | plastechservices.com | Visit | Company and capability information
Tank inspection | Fiberglass tank inspection | Open | Planning and qualified condition evaluation
Tank repair | Fiberglass tank repair | Open | Localized or structural FRP tank damage
Tank relining | Fiberglass tank relining | Open | Broader internal corrosion-barrier deterioration
Nozzle and flange | FRP tank nozzle and flange repair | Open | Connections, reinforced openings, and pipe-loading damage

## Tank Information
TANK INFORMATION
Complete what is known. Mark unknown information for follow-up and attach supporting records.
Section | Field | Facility record | Source / notes
Asset identification | Facility name
Asset identification | Site address
Asset identification | Area, unit, or process
Asset identification | Tank ID and asset number
Asset identification | Tank type
Asset identification | Manufacturer
Asset identification | Model or drawing number
Asset identification | Serial number
Asset identification | Year manufactured
Asset identification | Year installed
Asset identification | Orientation
Asset identification | Nominal capacity
Asset identification | Diameter
Asset identification | Shell height or vessel length
Asset identification | Roof or head configuration
Asset identification | Bottom configuration
Asset identification | Single-wall or double-wall
Asset identification | Secondary containment description
Construction and design | Resin system, if known
Construction and design | Reinforcement type, if known
Construction and design | Corrosion barrier or liner construction
Construction and design | Structural laminate construction
Construction and design | Exterior or UV protection system
Construction and design | Design pressure
Construction and design | Design vacuum
Construction and design | Design temperature
Construction and design | Specific gravity
Construction and design | Wind, seismic, or anchorage records
Construction and design | Nozzle schedule or drawing reference
Construction and design | Manufacturer instructions available
Service conditions | Current product
Service conditions | Chemical concentration or composition
Service conditions | Normal operating temperature
Service conditions | Maximum operating temperature
Service conditions | Normal liquid level
Service conditions | Fill and empty frequency
Service conditions | Agitation or mixing
Service conditions | Solids, slurry, crystals, or abrasive material
Service conditions | Vapor or gas exposure
Service conditions | Cleaning chemicals and methods
Service conditions | Operating pressure or vacuum
Service conditions | Venting arrangement
Service conditions | Prior products or service changes
Service conditions | Known chemistry, temperature, pressure, vacuum, or level excursions
Connected equipment and history | Inlet and outlet piping materials
Connected equipment and history | Pipe supports near the tank
Connected equipment and history | Flexible connections or expansion joints
Connected equipment and history | Valves, instruments, and other nozzle weight
Connected equipment and history | Pumps or equipment connected to the tank
Connected equipment and history | Mixer or agitator
Connected equipment and history | Ladders, platforms, handrails, and roof equipment
Connected equipment and history | Date of last external inspection
Connected equipment and history | Date of last internal inspection
Connected equipment and history | Previous reports and photographs available
Connected equipment and history | Previous leak or release
Connected equipment and history | Previous repairs or relining
Connected equipment and history | Nozzle or fitting modifications
Connected equipment and history | Foundation, anchor, or support work
Connected equipment and history | Known impact, fire, freeze, flood, wind, seismic, or vacuum event
Connected equipment and history | Current concerns from operations or maintenance

## Planning Checklist
PRE-INSPECTION PLANNING CHECKLIST
Coordinate the objective, records, operating state, access, facility controls, and qualified personnel before inspection.
Status | Section | Planning item | Owner | Reference / evidence | Notes
Not started | Records | Manufacturer drawings and data
Not started | Records | Material, laminate, resin, and corrosion-barrier information
Not started | Records | Chemical service, concentration, and temperature history
Not started | Records | Pressure, vacuum, venting, and liquid-level information
Not started | Records | Prior inspection reports, photographs, and condition maps
Not started | Records | Repair, reline, nozzle, piping, support, and foundation records
Not started | Records | Change-management records, work orders, and facility procedures
Not started | Coordination | Facility operations contact assigned
Not started | Coordination | EHS or safety contact assigned
Not started | Coordination | Tank operating state confirmed by the facility
Not started | Coordination | Product and hazard information available
Not started | Coordination | Area access, lighting, and working-at-height needs reviewed
Not started | Coordination | Weather, secondary containment, and nearby equipment considered
Not started | Coordination | Photography restrictions and documentation method reviewed
Not started | Coordination | Required permits and authorizations identified
Not started | Scope | Reason for inspection documented
Not started | Scope | Areas of concern and known changes documented
Not started | Scope | Required deliverables and comparison basis documented
Not started | Scope | Asset decision the inspection is intended to support documented
Not started | Scope | Qualified personnel responsible for methods and acceptance basis identified
Not started | Documentation | Workbook or approved digital form available
Not started | Documentation | Tank drawing or blank condition map available
Not started | Documentation | Camera, photo scale, and identification marker available
Not started | Documentation | Lighting and approved inspection equipment available
Not started | Briefing | Inspection scope and known conditions reviewed
Not started | Briefing | Access restrictions, communication, and escalation contacts reviewed

## External Walkdown
EXTERNAL FRP TANK WALKDOWN
Follow a repeatable route from the surroundings and supports to the bottom, shell, roof, connections, attachments, prior work, and overall shape.
Item | Observation status | Component / location | What is visible | Extent | Photo IDs | Follow-up status | Notes
Standing liquid, staining, deposits, or product in secondary containment | Not observed |  |  |  |  | Documented for record
Foundation cracking, settlement, unevenness, or support voids | Not observed |  |  |  |  | Documented for record
Tank tilt, movement, uplift, or flotation evidence | Not observed |  |  |  |  | Documented for record
Damaged anchors, lugs, saddles, skirts, or hold-downs | Not observed |  |  |  |  | Documented for record
Corroded, loose, or missing metallic hardware | Not observed |  |  |  |  | Documented for record
Color change, staining, fading, chalking, or loss of gloss | Not observed |  |  |  |  | Documented for record
Fiber blooming, fiber prominence, or exposed glass | Not observed |  |  |  |  | Documented for record
Crazing, matrix cracks, larger shell cracks, or whitening | Not observed |  |  |  |  | Documented for record
Scratches, gouges, cuts, grinding, impact, or crushing | Not observed |  |  |  |  | Documented for record
Blisters, bubbles, porosity, or voids | Not observed |  |  |  |  | Documented for record
Delamination, hollow areas, or disbonded secondary laminates | Not observed |  |  |  |  | Documented for record
Chemical spill or vapor exposure | Not observed |  |  |  |  | Documented for record
Softness, resin loss, unusual roughness, or abnormal surface texture | Not observed |  |  |  |  | Documented for record
Wrinkles, waviness, print-through, or geometric irregularity | Not observed |  |  |  |  | Documented for record
Bulging, out-of-roundness, buckling, or creep deformation | Not observed |  |  |  |  | Documented for record
Nozzle-to-shell or manway-to-shell cracking | Not observed |  |  |  |  | Documented for record
Nozzle-neck or flange laminate cracking | Not observed |  |  |  |  | Documented for record
Leakage, seepage, staining, or deposits at a connection | Not observed |  |  |  |  | Documented for record
Flange-face damage, forced fit-up, or gasket-related leakage | Not observed |  |  |  |  | Documented for record
Unsupported pipe, valve weight, misalignment, vibration, or thermal movement at a nozzle | Not observed |  |  |  |  | Documented for record
Cracking or movement at ladders, platforms, handrails, mixer mounts, or roof attachments | Not observed |  |  |  |  | Documented for record
Condition of repairs, patches, and exterior overlaminates | Not observed |  |  |  |  | Documented for record
Roof cracking, deformation, or collapse | Not observed |  |  |  |  | Documented for record
Evidence of pressure or vacuum damage | Not observed |  |  |  |  | Documented for record
Wind, flood, freeze, heat, fire, or seismic damage | Not observed |  |  |  |  | Documented for record
Active through-wall leakage or severe deformation | Not observed |  |  |  |  | Documented for record

## Internal Planning
INTERNAL INSPECTION PLANNING AND DOCUMENTATION
This workbook does not authorize tank entry. Complete internal records only under the facility's approved program and the direction of qualified personnel.
ENTRY-NEUTRAL SAFETY NOTE: The facility controls operating state, isolation, cleaning, decontamination, access classification, atmospheric evaluation, ventilation, permits, rescue provisions, PPE, and other requirements.
Item | Observation status | Component / location | What is visible | Extent | Photo IDs | Follow-up status | Notes
Discoloration, deposits, staining, or loss of gloss | Not observed |  |  |  |  | Documented for record
Roughness, softening, swelling, embrittlement, or other material change | Not observed |  |  |  |  | Documented for record
Resin loss, veil erosion, corrosion-barrier thinning, or washout | Not observed |  |  |  |  | Documented for record
Chemical attack, permeation, or absorption indicators | Not observed |  |  |  |  | Documented for record
Crazing, pinholes, pitting, matrix cracks, or liner cracks | Not observed |  |  |  |  | Documented for record
Blisters, blister rupture, bubbles, or porosity | Not observed |  |  |  |  | Documented for record
Exposed fibers, fiber attack, or fiber-matrix debonding | Not observed |  |  |  |  | Documented for record
Knuckle cracking or erosion | Not observed |  |  |  |  | Documented for record
Bottom degradation, cracking, sediment-related wear, or standing residue | Not observed |  |  |  |  | Documented for record
Drain-neck erosion or degradation | Not observed |  |  |  |  | Documented for record
Jet impingement opposite an inlet, return, sparger, or mixing device | Not observed |  |  |  |  | Documented for record
Abrasion, worn tracks, scraping, or cleaning damage | Not observed |  |  |  |  | Documented for record
Liner-to-structure disbondment or peeling | Not observed |  |  |  |  | Documented for record
Interlaminar delamination | Not observed |  |  |  |  | Documented for record
Voids, dry glass, incomplete wet-out, resin starvation, or resin-rich areas | Not observed |  |  |  |  | Documented for record
Wrinkles, folds, bridging, or reinforcement distortion | Not observed |  |  |  |  | Documented for record
Foreign inclusions or contamination | Not observed |  |  |  |  | Documented for record
Abnormal cure or hardness indications identified by qualified testing | Not observed |  |  |  |  | Documented for record
Uneven corrosion-barrier or structural thickness | Not observed |  |  |  |  | Documented for record
Chemical attack at nozzle bores, flange faces, necks, or transitions | Not observed |  |  |  |  | Documented for record
Nozzle-to-shell internal bond cracking | Not observed |  |  |  |  | Documented for record
Nozzle, manway, repad, or transition delamination | Not observed |  |  |  |  | Documented for record
Manway edge, neck, flange, or internal-surface degradation | Not observed |  |  |  |  | Documented for record
Abrasion, impact, or cracking from internal hardware, baffles, or mixers | Not observed |  |  |  |  | Documented for record
Structural cracks | Not observed |  |  |  |  | Documented for record
Fiber fracture | Not observed |  |  |  |  | Documented for record
Wall thinning or structural-laminate loss | Not observed |  |  |  |  | Documented for record
Thermal or mechanical fatigue indicators | Not observed |  |  |  |  | Documented for record
Repair, patch, liner, or reline deterioration | Not observed |  |  |  |  | Documented for record
Through-wall seepage, leakage, or severe structural change | Not observed |  |  |  |  | Documented for record

## Condition Atlas
99-CONDITION FRP TANK ATLAS
Educational reference only - not a visual diagnosis, fitness-for-service determination, or repair specification.
Rank | ID | Scope | Category | Condition | What you may notice | Why it matters | Inspection should confirm | Possible next step | Observation status | Location / photo IDs | Follow-up status | Relevant Plastech service | Service URL | Open service | Visual reference
Use the atlas to improve terminology and prepare questions. Actual appearance and scale vary; qualified inspection is required to confirm the condition and significance.
1 | E1 | External | Exterior surface condition | Exterior discoloration, staining, and loss of gloss | Color change, streaks, deposits, or dull patches indicate exposure or aging but do not prove structural damage. | Deposits can conceal deeper deterioration. | Whether the change is superficial, chemically active, or associated with softness, cracking, or fiber exposure. | Clean and reassess; restore compatible exterior surfacing if damage is shallow, or repair affected laminate if deterioration extends deeper. |  |  |  | Fiberglass tank repair | https://www.plastechservices.com/fiberglass-tank-repair | Open | Open visualizer
2 | E2 | External | Exterior surface condition | UV degradation, chalking, and exterior resin weathering | Fading, powdery chalk, roughness, and shallow cracks develop in the resin-rich exterior. | Progressive resin loss can expose reinforcement. | Degradation depth, fiber condition, cracking, and whether structural laminate is involved. | Renew a compatible UV-resistant resin surface or exterior overlaminate after qualified evaluation; deeper loss may require laminate reconstruction. |  |  |  | Fiberglass tank repair | https://www.plastechservices.com/fiberglass-tank-repair | Open | Open visualizer
3 | E3 | External | Exterior surface condition | Fiber blooming, fiber prominence, and exposed glass | White, threadlike glass becomes visible or raised as surface resin recedes or microcracks. | Exposed reinforcement has reduced environmental protection, although blooming alone is not a through-wall failure. | Whether fibers are merely prominent or chemically, mechanically, or structurally damaged. | Restore the resin-rich protective surface when shallow; remove and rebuild damaged laminate where fiber integrity is affected. |  |  |  | Fiberglass tank repair | https://www.plastechservices.com/fiberglass-tank-repair | Open | Open visualizer
4 | E4 | External | Exterior surface condition | External crazing and fine surface cracking | A network of fine hairline cracks appears in the exterior resin surface. | Crazing can remain superficial or become an entry path for moisture and further deterioration. | Crack depth, distribution, growth, and relation to loads or chemical exposure. | Restore compatible surface protection if confined to the resin-rich layer; reconstruct laminate if cracks extend beneath it. |  |  |  | Fiberglass tank repair | https://www.plastechservices.com/fiberglass-tank-repair | Open | Open visualizer
5 | E5 | External | Nozzles, flanges, and load transfer | Nozzle-to-shell bond cracking | Curved or radial cracks form at the nozzle fillet, secondary bond, or shell transition. | Cracking can weaken the connection and develop into leakage or separation. | Circumferential extent, depth, bond integrity, surrounding shell condition, and imposed piping loads. | Remove external loads and rebuild the secondary bond or nozzle connection where qualified assessment supports repair. |  |  |  | FRP tank nozzle and flange repair | https://www.plastechservices.com/fiberglass-tank-nozzle-repair | Open | Open visualizer
6 | E6 | External | Nozzles, flanges, and load transfer | Nozzle-neck cracking | Axial, circumferential, or localized cracks develop in the exposed nozzle neck. | The neck carries piping and containment loads and may leak or fracture as damage grows. | Crack depth, fiber involvement, nozzle geometry, and connected-system loads. | Correct the imposed load and reconstruct or replace the damaged nozzle neck as engineering evaluation directs. |  |  |  | FRP tank nozzle and flange repair | https://www.plastechservices.com/fiberglass-tank-nozzle-repair | Open | Open visualizer
7 | E7 | External | Nozzles, flanges, and containment | Nozzle weeping or leakage | Dampness, droplets, or a narrow liquid trail appears at the neck, repad, flange, or shell bond. | Any weep is a loss-of-containment indication and may conceal wider laminate damage. | Exact leak path, chemical exposure, damaged area, remaining laminate, and connection loads. | Isolate and make the tank safe, then remove unsound material and rebuild the qualified connection or replace it if damage is extensive. |  |  |  | FRP tank nozzle and flange repair | https://www.plastechservices.com/fiberglass-tank-nozzle-repair | Open | Open visualizer
8 | E8 | External | Nozzles, flanges, and containment | Flange leakage | Wetness or droplets emerge between mating flange faces. | Leakage can expose the flange, nozzle, shell, and nearby equipment to chemical attack. | Face condition, flatness, gasket compatibility, bolt condition, alignment, and laminate integrity. | Correct alignment and sealing components, or rebuild the flange if the FRP laminate itself is damaged. |  |  |  | FRP tank nozzle and flange repair | https://www.plastechservices.com/fiberglass-tank-nozzle-repair | Open | Open visualizer
9 | E9 | External | Nozzles and flanges | Flange-face damage and non-flatness | Scratches, chips, cracks, warpage, or an uneven mating gap interferes with gasket seating. | An uneven face can prevent reliable sealing and concentrate bolt load. | Damage depth, flatness, gasket contact, bolt pattern, and hub condition. | Restore or rebuild the qualified sealing surface, or replace the flange when geometry or laminate damage cannot be acceptably recovered. |  |  |  | FRP tank nozzle and flange repair | https://www.plastechservices.com/fiberglass-tank-nozzle-repair | Open | Open visualizer
10 | E10 | External | Nozzles and flanges | Flange laminate cracking or delamination | Cracks or separated laminate plies appear in the ring, hub, neck, or transition. | The flange may lose sealing stiffness or structural continuity. | Ply separation, crack depth, affected circumference, bolt-seat damage, and connected piping loads. | Unload the connection and rebuild or replace the damaged flange assembly based on qualified engineering evaluation. |  |  |  | FRP tank nozzle and flange repair | https://www.plastechservices.com/fiberglass-tank-nozzle-repair | Open | Open visualizer
11 | E11 | External | Nozzles and flanges | Improper bolt-torque damage or leakage | FRP is crushed or radially cracked below a washer, a gasket is extruded, or compression is visibly uneven. | Local crushing reduces flange capacity while uneven compression defeats the seal. | Bolt loading, gasket condition, flange-face damage, laminate crushing, and alignment. | Correct the bolting and gasket system and reconstruct damaged FRP where required by the governing connection design. |  |  |  | FRP tank nozzle and flange repair | https://www.plastechservices.com/fiberglass-tank-nozzle-repair | Open | Open visualizer
12 | E12 | External | Nozzles, flanges, and load transfer | Flange misalignment and forced fit-up | Pipe and nozzle axes are offset, flange faces meet unevenly, or the pipe appears pulled into position. | Forced fit-up imposes sustained bending and axial stress on the nozzle and shell. | Actual alignment, support condition, displacement source, bond damage, and allowable loads. | Realign and independently support the piping before repairing any damaged flange, neck, or shell bond. |  |  |  | FRP tank nozzle and flange repair | https://www.plastechservices.com/fiberglass-tank-nozzle-repair | Open | Open visualizer
13 | E13 | External | Nozzles and load transfer | Connected-pipe dead-load damage at nozzles | A nozzle sags or distorts, often with whitening or cracking near the loaded side of its bond. | Sustained load can cause creep, cracking, bond failure, or nozzle separation. | Pipe support, imposed forces, permanent deformation, crack depth, and surrounding shell condition. | Transfer piping weight to proper supports, then rebuild or replace the damaged connection as qualified analysis permits. |  |  |  | FRP tank nozzle and flange repair | https://www.plastechservices.com/fiberglass-tank-nozzle-repair | Open | Open visualizer
14 | E14 | External | Nozzles and load transfer | Thermal-expansion load damage at nozzles | Directional nozzle displacement, opposing bond cracks, or localized stress whitening indicates restrained movement. | Repeated or sustained thermal load can fatigue the nozzle and shell bond. | Operating temperature range, movement direction, restraint system, crack depth, and nozzle capacity. | Correct the piping flexibility or restraint condition and reconstruct the affected connection if it remains repairable. |  |  |  | FRP tank nozzle and flange repair | https://www.plastechservices.com/fiberglass-tank-nozzle-repair | Open | Open visualizer
15 | E15 | External | Connections and cyclic loading | Vibration and fatigue damage at nozzles or attachments | Multiple short, similarly oriented cracks or a whitening halo develops around a nozzle or attachment. | Repeated loading can progressively grow matrix cracks, delamination, and bond damage. | Vibration source, frequency and history, crack growth, delamination, and load path. | Eliminate or isolate the cyclic load, then rebuild affected laminate or replace the connection where required. |  |  |  | FRP tank nozzle and flange repair | https://www.plastechservices.com/fiberglass-tank-nozzle-repair | Open | Open visualizer
16 | E16 | External | Exterior chemical exposure | External chemical attack from spills, overflow, or vapors | A spill path shows bleaching, roughness, softened gloss, resin loss, or exposed fibers. | External exposure can degrade structural laminate, attachments, base areas, and connected piping. | Chemical identity, concentration, exposure duration, affected depth, and fiber condition. | Decontaminate and stop the exposure, then restore compatible surfacing or rebuild degraded laminate according to qualified material selection. |  |  |  | Fiberglass tank relining | https://www.plastechservices.com/fiberglass-tank-reline | Open | Open visualizer
17 | E17 | External | External mechanical damage | Surface scratches, gouges, cuts, and grinding damage | Linear scratches or localized gouges remove smooth resin and may reveal pale reinforcement. | Cut fibers or lost resin protection can create a stress concentration and exposure path. | Depth, fiber severance, location, wall thickness, and any hidden delamination. | Seal or restore shallow resin loss; remove and reconstruct laminate when reinforcement has been damaged. |  |  |  | Fiberglass tank repair | https://www.plastechservices.com/fiberglass-tank-repair | Open | Open visualizer
18 | E18 | External | External mechanical damage | Impact damage, indentation, and crushing | A dent, white stress halo, radial cracks, or crushed surface marks a concentrated impact. | Subsurface delamination may extend beyond the visible mark. | Impact extent, delamination, fiber fracture, residual shape, and remaining laminate. | Reconstruct a localized area if damage is bounded and repairable; extensive crushing or loss of shape may require section or tank replacement. |  |  |  | Fiberglass tank repair | https://www.plastechservices.com/fiberglass-tank-repair | Open | Open visualizer
19 | E19 | External | Shell laminate damage | External matrix cracking and larger shell cracks | A distinct crack extends beyond fine surface crazing and may branch across the shell. | A larger crack can connect to delamination, fiber damage, or leakage. | Depth, length, orientation, growth, fiber involvement, and initiating load. | Correct the cause and perform engineered laminate reconstruction where remaining structure qualifies; replace where damage is extensive. |  |  |  | Fiberglass tank repair | https://www.plastechservices.com/fiberglass-tank-repair | Open | Open visualizer
20 | E20 | External | Shell laminate damage | External delamination and hollow areas | A subtly raised, whitened, or hollow-sounding area indicates separation between laminate plies. | Visible surface change may understate the separated area and reduced load transfer. | Delamination perimeter, depth, interfaces, moisture, and structural significance. | Remove and rebuild separated laminate when localized; widespread or deep delamination may require larger reconstruction or replacement. |  |  |  | Fiberglass tank repair | https://www.plastechservices.com/fiberglass-tank-repair | Open | Open visualizer
21 | E21 | External | Secondary bonds and attachments | Repad or secondary-laminate disbonding | An edge lifts from a nozzle pad, manway pad, lug overlay, platform pad, or repair laminate. | The attachment may no longer transfer load as intended. | Bonded area, substrate condition, load path, cure history, and cause of separation. | Remove the disbonded work, correct the load or preparation issue, and rebuild the qualified secondary laminate. |  |  |  | Fiberglass tank repair | https://www.plastechservices.com/fiberglass-tank-repair | Open | Open visualizer
22 | E22 | External | Manways and penetrations | Manway-neck and manway-to-shell cracking | Curved or radial cracks appear at the manway neck, fillet, or shell transition. | The opening interrupts shell continuity and can develop leakage or local structural failure. | Crack depth, bond extent, shell deformation, flange loading, and access-related damage. | Rebuild the transition or manway connection after correcting the contributing load and confirming surrounding laminate integrity. |  |  |  | FRP tank nozzle and flange repair | https://www.plastechservices.com/fiberglass-tank-nozzle-repair | Open | Open visualizer
23 | E23 | External | Manways and containment | Manway flange, cover, gasket, or fastener leakage | Wetness emerges at the cover gasket, often near unevenly seated bolts or an extruded gasket. | Leakage exposes a large opening and adjacent shell to chemical attack. | Cover and flange geometry, gasket compatibility, bolt loading, cracks, and neck condition. | Correct sealing and hardware deficiencies; rebuild or replace damaged FRP manway components where necessary. |  |  |  | FRP tank nozzle and flange repair | https://www.plastechservices.com/fiberglass-tank-nozzle-repair | Open | Open visualizer
24 | E24 | External | Prior repair failure | Repair-patch or external-overlaminate failure | A previous patch cracks, peels, blisters, lifts, or differs sharply from the surrounding laminate. | The repair may conceal continuing deterioration or transfer stress to adjacent laminate. | Original damage, substrate condition, compatibility, bond extent, and present loads. | Remove the failed repair, reassess the complete damage zone, and redesign the repair—or replace the affected component—using a qualified system. |  |  |  | Fiberglass tank repair | https://www.plastechservices.com/fiberglass-tank-repair | Open | Open visualizer
25 | E25 | External | Fabrication and laminate quality | Dry glass and incomplete wet-out | Cloudy white or opaque reinforcement remains visibly under-saturated with resin. | The area has reduced chemical protection and interlaminar continuity. | Size, depth, ply location, surface connectivity, and structural or barrier significance. | Remove and rebuild unacceptable defective laminate; disposition of minor indications requires governing criteria and qualified evaluation. |  |  |  | Fiberglass tank repair | https://www.plastechservices.com/fiberglass-tank-repair | Open | Open visualizer
26 | E26 | External | Fabrication and laminate quality | Voids, air pockets, porosity, and bubbles | Small subsurface cavities or larger irregular air pockets interrupt an otherwise continuous laminate. | Voids reduce continuity and may seed moisture entry, blistering, delamination, or leakage. | Size, density, depth, interfaces, and connection to either surface. | Locally remove and rebuild significant defects; widespread porosity may require broader laminate reconstruction or replacement. |  |  |  | Fiberglass tank repair | https://www.plastechservices.com/fiberglass-tank-repair | Open | Open visualizer
27 | E27 | External | Fabrication and laminate quality | Resin-starved or resin-rich areas | A matte, fiber-prominent region lies beside a glossy or amber resin pocket, sometimes with shrinkage cracks. | Starved zones expose reinforcement; resin-rich zones can be brittle and glass-deficient. | Area, depth, reinforcement content, cracking, and effect on barrier or structural performance. | Remove and rebuild materially deficient laminate where qualified acceptance criteria are not met. |  |  |  | Fiberglass tank repair | https://www.plastechservices.com/fiberglass-tank-repair | Open | Open visualizer
28 | E28 | External | Fabrication and laminate quality | Wrinkles, bridging, waviness, and fiber distortion | Raised folds, bridged hollows, or distorted fiber paths interrupt smooth laminate geometry. | The condition can create resin pockets, thin zones, weak directions, and stress concentrations. | Ply distortion, thickness, voiding, affected area, and load orientation. | Reconstruct localized defective laminate or provide engineered reinforcement when the surrounding structure and governing design permit it. |  |  |  | Fiberglass tank repair | https://www.plastechservices.com/fiberglass-tank-repair | Open | Open visualizer
29 | E29 | External | Fabrication and bond quality | Foreign inclusions or laminate contamination | Dirt, moisture, wax, dust, or another inclusion is trapped beneath resin, sometimes with a discolored halo or nearby voids. | Contamination can reduce adhesion, cure quality, and durability. | Material, size, depth, interface, and whether a bond or structural ply is interrupted. | Remove contaminated material and rebuild the affected laminate when its location or extent is unacceptable. |  |  |  | Fiberglass tank repair | https://www.plastechservices.com/fiberglass-tank-repair | Open | Open visualizer
30 | E30 | External | Cure and material condition | Improper cure, low hardness, or exterior softness | Uneven gloss, amber color, softness, impressions, burn discoloration, shrinkage cracks, or voids indicate abnormal cure. | The laminate may have inadequate chemical or mechanical properties. | Affected depth and area, hardness pattern, resin condition, service exposure, and associated cracking or delamination. | Remove and rebuild unsound undercured or heat-damaged laminate unless a qualified material evaluation establishes another acceptable disposition. |  |  |  | Fiberglass tank repair | https://www.plastechservices.com/fiberglass-tank-repair | Open | Open visualizer
31 | E31 | External | Fabrication and structural capacity | Uneven thickness, thin laminate, or missing reinforcement | Local depressions or geometry changes may mark a thin area or absent reinforcement. | Local capacity and stiffness may fall below the intended load path. | Actual thickness, ply content, affected dimensions, design loads, and deformation. | Add engineered compatible reinforcement or reconstruct the area only after confirming the original design basis; replacement may be necessary if deficiency is widespread. |  |  |  | Fiberglass tank repair | https://www.plastechservices.com/fiberglass-tank-repair | Open | Open visualizer
32 | E32 | External | Surface and fabrication condition | Print-through, waviness, and geometric irregularity | Fiber patterns, ripples, or low-amplitude geometry become visible under glancing light. | The condition may be cosmetic or may accompany local thinness or load concentration. | Whether thickness, stiffness, bonding, or structural shape is affected. | Refinish a verified cosmetic condition; reconstruct or reinforce only when assessment identifies material or structural deficiency. |  |  |  | Fiberglass tank repair | https://www.plastechservices.com/fiberglass-tank-repair | Open | Open visualizer
33 | E33 | External | Global structural condition | Shell deformation, bulging, and out-of-roundness | A broad shell quadrant moves outward or loses cylindrical geometry. | Deformation redistributes load to nozzles, attachments, and adjacent laminate. | Geometry, progression, pressure history, support, wall construction, cracks, and delamination. | Correct the initiating load or support condition and use engineered reinforcement, reconstruction, or replacement according to remaining capacity. |  |  |  | Fiberglass tank repair | https://www.plastechservices.com/fiberglass-tank-repair | Open | Open visualizer
34 | E34 | External | Global structural condition | Creep deformation | Permanent sagging or smooth long-term bulging appears near sustained shell, nozzle, attachment, or roof loads. | Increasing strain can precede cracking, delamination, or rupture. | Deformation history, sustained loads, temperature, laminate condition, and residual geometry. | Reduce the sustained load and evaluate engineered reinforcement or replacement; a cosmetic surface treatment does not address creep. |  |  |  | Fiberglass tank repair | https://www.plastechservices.com/fiberglass-tank-repair | Open | Open visualizer
35 | E35 | External | Cyclic structural damage | Mechanical or thermal fatigue cracking | Families of short cracks grow near a repeatedly loaded nozzle, attachment, roof transition, or shell zone. | Damage can continue below the visible surface and enlarge with each cycle. | Load history, crack growth, delamination, fiber condition, and affected stress path. | Control the cyclic source, then reconstruct or replace damaged laminate based on engineered remaining-capacity evaluation. |  |  |  | Fiberglass tank repair | https://www.plastechservices.com/fiberglass-tank-repair | Open | Open visualizer
36 | E36 | External | Foundation and support | Foundation settlement and tank tilt | The tank leans, one knuckle is compressed, a base gap opens, or piping becomes misaligned. | Settlement overloads the bottom, knuckle, anchors, nozzles, and connected piping. | Tank geometry, foundation condition, bottom support, anchor loads, and secondary laminate damage. | Stabilize and restore the support condition before repairing affected tank components or replacing the tank if distortion is unrecoverable. |  |  |  | Fiberglass tank repair | https://www.plastechservices.com/fiberglass-tank-repair | Open | Open visualizer
37 | E37 | External | Foundation and support | Bottom-support voids or foundation irregularity | A localized base gap, washout, debris point, or missing support permits bottom flexure. | Concentrated bottom and knuckle stresses can create cracks or delamination. | Full support profile, bottom deformation, knuckle damage, foundation drainage, and settlement. | Correct the continuous support condition, then repair damaged bottom or knuckle laminate if qualified assessment confirms repairability. |  |  |  | Fiberglass tank repair | https://www.plastechservices.com/fiberglass-tank-repair | Open | Open visualizer
38 | E38 | External | Anchors and supports | Anchor-lug or hold-down damage | Cracked overlays, lifted lug laminates, elongated holes, or damaged bolts appear at a hold-down. | Anchor failure can damage the parent shell or permit tank movement. | Anchor design, load history, bolt condition, overlay bond, shell damage, and foundation attachment. | Rebuild the engineered lug and overlay, renew hardware, and correct restraint deficiencies where the surrounding shell remains suitable. |  |  |  | Fiberglass tank repair | https://www.plastechservices.com/fiberglass-tank-repair | Open | Open visualizer
39 | E39 | External | Attachments and local load transfer | Ladder, platform, handrail, mixer, and roof-attachment damage | Indentation, whitening, cracks, or shifted pads appear around an attachment. | Attachment loads can crack the pad and underlying shell or roof. | Actual load path, hardware stability, bond condition, crack depth, and parent-laminate damage. | Remove or redistribute the load, then rebuild the qualified attachment laminate or supporting tank area. |  |  |  | Fiberglass tank repair | https://www.plastechservices.com/fiberglass-tank-repair | Open | Open visualizer
40 | E40 | External | Attachments and hardware | Corroded, loose, or failed metallic attachments and hardware | Metal bolts, clips, supports, or ladder parts show corrosion, looseness, or failure, sometimes staining the FRP. | Failed hardware can lose function or impose point loads and abrasion on the composite. | Metal loss, remaining attachment function, FRP contact damage, and load transfer. | Replace compatible hardware and repair any locally crushed, worn, or cracked FRP after confirming the attachment design. |  |  |  | Fiberglass tank repair | https://www.plastechservices.com/fiberglass-tank-repair | Open | Open visualizer
41 | E41 | External | Global structural instability | Shell buckling or wrinkling | Broad circumferential or localized folds alternate inward and outward in the shell. | Buckling indicates loss of geometric stability and may damage multiple laminate layers. | Cause, residual shape, cracking, delamination, stiffness, and affected circumference. | Correct the destabilizing condition; engineered reconstruction is possible only where residual laminate qualifies, otherwise replacement may be required. |  |  |  | Fiberglass tank repair | https://www.plastechservices.com/fiberglass-tank-repair | Open | Open visualizer
42 | E42 | External | Pressure/vacuum failure | Vacuum buckling or implosion | The upper shell or roof is pulled inward with broad concave deformation and buckle ridges. | Global collapse can damage shell, roof, nozzles, and laminate interfaces simultaneously. | Venting event, full deformation, cracking, delamination, and remaining structural geometry. | Correct the venting cause and obtain engineered disposition; extensive implosion damage commonly points toward major reconstruction or replacement. |  |  |  | Fiberglass tank repair | https://www.plastechservices.com/fiberglass-tank-repair | Open | Open visualizer
43 | E43 | External | Pressure/vacuum failure | Overpressure bulging and cracking | The upper shell or roof bulges outward and may crack around transitions or fittings. | An atmospheric or low-pressure tank may have exceeded its intended load capability. | Pressure event, venting, deformation, crack and fiber damage, and global tank geometry. | Correct process and venting deficiencies; use engineered reconstruction only if remaining structure qualifies, otherwise replace. |  |  |  | Fiberglass tank repair | https://www.plastechservices.com/fiberglass-tank-repair | Open | Open visualizer
44 | E44 | External | Roof and global structure | Roof cracking or collapse | A roof depression, radial cracking, or displaced fitting indicates localized or broad roof failure. | Roof damage can compromise venting, openings, weather protection, and shell-transition loads. | Crack depth, deformation, attachments, roof-support design, and shell-joint condition. | Remove the initiating load and rebuild or replace the roof and transition according to a qualified structural assessment. |  |  |  | Fiberglass tank repair | https://www.plastechservices.com/fiberglass-tank-repair | Open | Open visualizer
45 | E45 | External | Environmental and global loading | Wind damage | Directional shell or roof buckling, strained anchors, or displaced attachments follows a wind event. | Damage can affect the tank, anchors, foundation, roof, and piping as one system. | Alignment, shell and roof damage, anchor loads, foundation condition, and connected piping. | Restore anchorage and load paths, then perform engineered repairs or replace components according to the full-system assessment. |  |  |  | Fiberglass tank repair | https://www.plastechservices.com/fiberglass-tank-repair | Open | Open visualizer
46 | E46 | External | Environmental and foundation loading | Uplift or flotation | The base lifts, anchors stretch or fail, and lower piping moves out of alignment. | Uplift can damage the bottom, knuckle, anchors, nozzles, and piping simultaneously. | Bottom shape, anchor and foundation condition, piping displacement, and hidden laminate damage. | Reestablish support and buoyancy restraint, then repair or replace affected tank and connection components as engineering evaluation directs. |  |  |  | Fiberglass tank repair | https://www.plastechservices.com/fiberglass-tank-repair | Open | Open visualizer
47 | E47 | External | Environmental and localized pressure | Freeze damage | A nozzle, drain, jacket, or low point bulges or splits, sometimes with a crack into adjacent laminate. | Local expansion can fracture a connection or create a through-wall path. | Full crack extent, trapped-volume location, surrounding laminate, and recurring freeze exposure. | Eliminate the liquid trap or freezing condition and rebuild or replace the affected connection and adjacent laminate. |  |  |  | Fiberglass tank repair | https://www.plastechservices.com/fiberglass-tank-repair | Open | Open visualizer
48 | E48 | External | Thermal damage | Fire, heat, charring, or thermal decomposition | Tan-to-black discoloration, charring, blistered resin, distortion, or exposed fibers follows external heat. | Resin properties and laminate bonds can be lost beyond the visible charred area. | Temperature exposure, damage depth and area, softness or embrittlement, delamination, and fiber condition. | Remove all heat-damaged material and reconstruct only where qualified evaluation confirms sound surrounding laminate; extensive exposure may require replacement. |  |  |  | Fiberglass tank repair | https://www.plastechservices.com/fiberglass-tank-repair | Open | Open visualizer
49 | E49 | External | Environmental and global loading | Seismic damage | Tank shift, anchor cracking, knuckle whitening, and nozzle or piping misalignment occur in a common direction. | Multiple components can be damaged even when the shell remains standing. | Global alignment, bottom, anchors, shell, roof, nozzles, attachments, and piping. | Reestablish foundation, restraint, and piping conditions, then use engineered component repairs or replacement based on the complete system inspection. |  |  |  | Fiberglass tank repair | https://www.plastechservices.com/fiberglass-tank-repair | Open | Open visualizer
50 | E50 | External | Severe connection failure | Nozzle pullout or separation | The nozzle bond opens or the connection partially separates, exposing layered FRP edges and radial shell cracks. | Structural continuity and containment at the penetration are substantially reduced. | Surrounding shell damage, separation extent, remaining bond, pipe loads, and chemical exposure. | Isolate the tank, support the piping, and reconstruct or replace the nozzle and affected shell only under an engineered repair design. |  |  |  | FRP tank nozzle and flange repair | https://www.plastechservices.com/fiberglass-tank-nozzle-repair | Open | Open visualizer
51 | E51 | External | Containment failure | Through-wall shell crack or active shell leak | Seepage, a stream, or spray emerges from a crack that crosses the corrosion barrier and structural wall. | The tank has lost containment and may have broader unseen damage. | Safe isolation, crack extent, surrounding wall condition, root cause, and remaining structural capacity. | Keep the asset out of service until an engineered laminate repair, reline, major reconstruction, or replacement is selected. |  |  |  | Fiberglass tank repair | https://www.plastechservices.com/fiberglass-tank-repair | Open | Open visualizer
52 | E52 | External | Catastrophic containment failure | Creep rupture or catastrophic shell rupture | A large irregular opening with peeled laminate plies and broken fibers follows rapid structural separation. | Major containment and structural integrity are lost. | Event cause, full tank damage, foundation and connection effects, and whether any structure remains reusable. | Replacement is generally the primary consideration; any proposed reconstruction requires a qualified, asset-specific engineering basis. |  |  |  | Fiberglass tank repair | https://www.plastechservices.com/fiberglass-tank-repair | Open | Open visualizer
53 | E53 | External | Catastrophic containment failure | Bottom blowout | The bottom or bottom-to-shell joint separates, often with failed anchors and a major release at the base. | The primary load-carrying and containment boundary has failed. | Bottom, knuckle, anchors, foundation, shell distortion, event sequence, and surrounding equipment. | Tank replacement is generally indicated; major engineered reconstruction should be considered only if a comprehensive evaluation supports it. |  |  |  | Fiberglass tank repair | https://www.plastechservices.com/fiberglass-tank-repair | Open | Open visualizer
54 | I1 | Internal | Internal surface and corrosion barrier | Inner-surface resin attack and normal-to-abnormal resin degradation | The resin-rich surface becomes dull, rough, soft, discolored, or locally depleted; normal aging must be separated from progressive damage. | The corrosion barrier is the first protection for the structural laminate. | Exposure history, affected depth and area, material change, and progression. | Restore the compatible inner surface when damage is shallow; deeper or widespread deterioration may require laminate repair, relining, or replacement. |  |  |  | Fiberglass tank relining | https://www.plastechservices.com/fiberglass-tank-reline | Open | Open visualizer
55 | I2 | Internal | Internal surface and corrosion barrier | Chemical attack of the corrosion barrier | Whitening, amber discoloration, roughness, pitting, or softening spreads through the veil and resin-rich liner. | Continued attack can reach structural laminate. | Chemical compatibility, operating history, barrier thickness, attack depth, and fiber exposure. | Remove degraded material and rebuild a qualified compatible barrier, or reline or replace where attack is extensive. |  |  |  | Fiberglass tank relining | https://www.plastechservices.com/fiberglass-tank-reline | Open | Open visualizer
56 | I3 | Internal | Internal surface and corrosion barrier | Permeation and chemical absorption | Diffuse discoloration, subsurface darkening, swelling, softness, or blistering indicates fluid or vapor movement into resin. | Damage can extend beyond visible surface change. | Penetration depth, material-property change, affected area, chemical service, and structural involvement. | Restore the barrier if effects are shallow and bounded; deeper permeation may require relining, laminate reconstruction, or replacement. |  |  |  | Fiberglass tank relining | https://www.plastechservices.com/fiberglass-tank-reline | Open | Open visualizer
57 | I4 | Internal | Internal surface and corrosion barrier | Veil erosion | The smooth surfacing veil is worn away, revealing coarser glass texture below. | Loss of veil reduces the resin-rich protective layer. | Remaining barrier thickness, exposed reinforcement, affected area, and active erosion source. | Mitigate the exposure and restore the compatible veil and corrosion barrier where surrounding laminate remains sound. |  |  |  | Fiberglass tank relining | https://www.plastechservices.com/fiberglass-tank-reline | Open | Open visualizer
58 | I5 | Internal | Internal surface and corrosion barrier | Corrosion-barrier thinning, erosion, or washout | A worn channel or broad shallow area shows reduced liner thickness toward the structural laminate. | Remaining chemical protection and service margin are reduced. | Residual barrier, structural-wall involvement, full extent, and continuing exposure. | Rebuild the barrier or install a qualified reline after correcting the cause; widespread structural loss may require replacement. |  |  |  | Fiberglass tank relining | https://www.plastechservices.com/fiberglass-tank-reline | Open | Open visualizer
59 | I6 | Internal | Internal surface and corrosion barrier | Internal discoloration, staining, deposits, and loss of gloss | Liquid-level rings, streaks, crystalline deposits, or dull zones record service exposure but may conceal the substrate. | Visual appearance alone cannot establish remaining strength, and deposits may mask damage. | Condition after safe cleaning, substrate hardness and texture, cracking, and exposure history. | Clean and reassess; repair only the confirmed underlying damage rather than treating staining itself as structural failure. |  |  |  | Fiberglass tank relining | https://www.plastechservices.com/fiberglass-tank-reline | Open | Open visualizer
60 | I7 | Internal | Internal surface and corrosion barrier | Crazing and fine inner-surface cracks | Dense networks of hairline cracks remain at or near the resin-rich surface. | Crazing can become a pathway for deeper chemical entry. | Crack depth, distribution, growth, chemical exposure, and underlying laminate condition. | Restore a compatible barrier where cracks are superficial; reconstruct deeper laminate where crazing has progressed. |  |  |  | Fiberglass tank relining | https://www.plastechservices.com/fiberglass-tank-reline | Open | Open visualizer
61 | I8 | Internal | Internal surface and corrosion barrier | Osmotic, chemical, gas, or vapor blistering | Intact rounded or elongated blisters rise beneath the liner or inner surface. | Blisters can rupture, expose reinforcement, or signal wider disbondment. | Number, size, depth, contents, interface, distribution, and surrounding bond condition. | Remove and rebuild localized unsound blistered material; broad blistering may favor a qualified reline or replacement. |  |  |  | Fiberglass tank relining | https://www.plastechservices.com/fiberglass-tank-reline | Open | Open visualizer
62 | I9 | Internal | Internal surface and corrosion barrier | Blister rupture | An opened blister has curled resin edges and exposed glass or deeper laminate. | The opening accelerates chemical entry and erosion. | Cavity depth, exposed fibers, surrounding blisters, chemical penetration, and structural involvement. | Remove the ruptured and disbonded material and rebuild the compatible barrier or laminate after determining the full affected area. |  |  |  | Fiberglass tank relining | https://www.plastechservices.com/fiberglass-tank-reline | Open | Open visualizer
63 | I10 | Internal | Structural damage and material change | Internal matrix or resin cracking | A distinct crack penetrates farther than crazing but may leave most fibers intact. | Matrix cracks can connect to delamination or a leak path. | Depth, direction, fiber condition, delamination, growth, and initiating load. | Correct the cause and perform engineered laminate restoration where damage is bounded; extensive cracking may require replacement. |  |  |  | Fiberglass tank relining | https://www.plastechservices.com/fiberglass-tank-reline | Open | Open visualizer
64 | I11 | Internal | Internal surface and corrosion barrier | Exposed glass fibers and fiber attack | Pale reinforcement becomes visible, etched, softened, or frayed after resin loss. | Direct process contact can degrade reinforcement and reduce structural capacity. | Fiber condition, damage depth, affected area, chemical exposure, and remaining wall. | Remove attacked laminate and rebuild the barrier and structural plies, or reline or replace if damage is widespread. |  |  |  | Fiberglass tank relining | https://www.plastechservices.com/fiberglass-tank-reline | Open | Open visualizer
65 | I12 | Internal | Structural damage and material change | Knuckle-radius erosion and cracking | Veil loss, scoring, whitening, or cracks follow the internal shell-to-bottom radius. | The knuckle is a critical geometric and load transition. | Crack depth, residual barrier, bottom support, settlement, and structural laminate. | Correct support or abrasion causes, then rebuild the qualified knuckle barrier or laminate where repairability is established. |  |  |  | Fiberglass tank relining | https://www.plastechservices.com/fiberglass-tank-reline | Open | Open visualizer
66 | I13 | Internal | Structural damage and material change | Bottom-surface degradation and cracking | Dullness, resin loss, deposits, and branching cracks affect the internal bottom. | Bottom damage can progress unseen toward leakage or joint failure. | Foundation support, crack depth, wall loss, chemical attack, and bottom-to-shell condition. | Correct the support condition and perform engineered bottom repair or relining; broad structural damage may require replacement. |  |  |  | Fiberglass tank relining | https://www.plastechservices.com/fiberglass-tank-reline | Open | Open visualizer
67 | I14 | Internal | Internal connections and hardware | Drain-nozzle neck erosion and degradation | Directional scoring, thinning, rough resin, or veil exposure affects the drain bore and transition. | Concentrated damage at a drain can breach the connection or surrounding bottom. | Residual wall, flow path, chemical attack, bond integrity, and bottom involvement. | Correct the erosive condition and rebuild or replace the drain and transition using a qualified compatible laminate system. |  |  |  | FRP tank nozzle and flange repair | https://www.plastechservices.com/fiberglass-tank-nozzle-repair | Open | Open visualizer
68 | I15 | Internal | Internal surface and corrosion barrier | Inlet, return, sparger, or jet-impingement damage | A fan-shaped or elongated wear patch forms directly opposite a nozzle or mixing device. | Local erosion can rapidly thin the corrosion barrier. | Flow direction, exposure rate, depth, barrier remaining, and structural involvement. | Modify the damaging flow condition where necessary and rebuild the affected barrier or laminate. |  |  |  | Fiberglass tank relining | https://www.plastechservices.com/fiberglass-tank-reline | Open | Open visualizer
69 | I16 | Internal | Internal surface and corrosion barrier | Internal abrasion | Scrape marks, worn tracks, and roughened veil appear on the bottom or lower wall. | Repeated wear removes resin and can expose or sever reinforcement. | Abrasion source, affected area and depth, fiber damage, and remaining wall. | Mitigate the abrasion and restore compatible surface or laminate; widespread service exposure may justify a qualified protective reline. |  |  |  | Fiberglass tank relining | https://www.plastechservices.com/fiberglass-tank-reline | Open | Open visualizer
70 | I17 | Internal | Internal surface and corrosion barrier | Pitting, pinholes, and localized resin loss | Small cavities or porous openings interrupt the inner resin surface. | Pits can expose deeper laminate or form permeation and leak paths. | Whether openings are blind or through-wall, their density, depth, cause, and surrounding laminate condition. | Remove and rebuild localized defective barrier; widespread pitting may require broader relining or replacement. |  |  |  | Fiberglass tank relining | https://www.plastechservices.com/fiberglass-tank-reline | Open | Open visualizer
71 | I18 | Internal | Structural damage and material change | Liner cracking | A defined crack opens through the corrosion liner while the structural wall may still appear intact. | The protective liner is breached and process fluid can reach the structural laminate. | Crack depth, liner bond, structural-wall condition, cause, and affected extent. | Reconstruct the localized liner or install a qualified reline; repair must also address any underlying structural damage. |  |  |  | Fiberglass tank relining | https://www.plastechservices.com/fiberglass-tank-reline | Open | Open visualizer
72 | I19 | Internal | Laminate and fabrication | Liner-to-structure disbondment and peeling | The liner, coating, or reline lifts, curls, flakes, or separates from the structural substrate. | The separated liner no longer protects or transfers load uniformly. | Bonded area, substrate soundness, trapped fluid, compatibility, and full disbondment extent. | Remove disbonded material and reline only a qualified, properly prepared substrate; replace where substrate deterioration is too extensive. |  |  |  | Fiberglass tank relining | https://www.plastechservices.com/fiberglass-tank-reline | Open | Open visualizer
73 | I20 | Internal | Laminate and fabrication | Interlaminar delamination | A raised or hollow area marks separation between internal wall plies. | Separated plies cannot transfer load as intended. | Perimeter, depth, interfaces, moisture or chemical intrusion, and structural significance. | Remove and rebuild localized delamination; deep or widespread separation may require major reconstruction or replacement. |  |  |  | Fiberglass tank relining | https://www.plastechservices.com/fiberglass-tank-reline | Open | Open visualizer
74 | I21 | Internal | Laminate and fabrication | Fiber-matrix debonding and stress whitening | Diffuse white regions indicate microscopic separation between resin and fibers, often near strain or cracking. | Interface damage can reduce stiffness and precede cracks or fiber fracture, although whitening is not automatically rejectable. | Cause, depth, active load, fiber integrity, and associated delamination. | Remove the load and rebuild confirmed damaged laminate when required by qualified evaluation. |  |  |  | Fiberglass tank relining | https://www.plastechservices.com/fiberglass-tank-reline | Open | Open visualizer
75 | I22 | Internal | Laminate and fabrication | Dry glass and incomplete wet-out | Cloudy white or opaque reinforcement remains insufficiently saturated with resin. | The area has poor barrier continuity and interlaminar performance. | Size, depth, ply location, surface connection, and effect on chemical or structural service. | Remove and rebuild unacceptable dry laminate; disposition of minor indications must follow the governing criteria. |  |  |  | Fiberglass tank relining | https://www.plastechservices.com/fiberglass-tank-reline | Open | Open visualizer
76 | I23 | Internal | Laminate and fabrication | Voids, air pockets, bubbles, and porosity | Irregular subsurface cavities or elongated air pockets interrupt the inner laminate. | Voids can seed blistering, cracking, delamination, and leakage. | Size, density, depth, interfaces, surface connectivity, and location in the barrier or structural wall. | Repair localized significant defects by qualified removal and reconstruction; widespread porosity may require broader reline or laminate replacement. |  |  |  | Fiberglass tank relining | https://www.plastechservices.com/fiberglass-tank-reline | Open | Open visualizer
77 | I24 | Internal | Laminate and fabrication | Resin starvation or resin-rich areas | Fiber-prominent matte zones or glossy amber resin pockets show an unbalanced resin-to-glass ratio. | Starved areas are porous and exposed; resin-rich areas may be brittle and crack-prone. | Extent, reinforcement content, cracking, barrier continuity, and structural significance. | Remove and rebuild materially deficient laminate according to qualified acceptance and design criteria. |  |  |  | Fiberglass tank relining | https://www.plastechservices.com/fiberglass-tank-reline | Open | Open visualizer
78 | I25 | Internal | Laminate and fabrication | Wrinkles, folds, bridging, and reinforcement distortion | Folded fibers, bridged hollows, and resin pockets disrupt the intended laminate path. | The defect can create thin spots, voids, weak directions, and concentrated stress. | Ply geometry, missing thickness, affected area, voiding, and load orientation. | Reconstruct localized defective laminate or provide engineered reinforcement only where the original design and surrounding material support it. |  |  |  | Fiberglass tank relining | https://www.plastechservices.com/fiberglass-tank-reline | Open | Open visualizer
79 | I26 | Internal | Laminate and fabrication | Foreign inclusions and contamination | A trapped dark or cloudy inclusion, often with nearby voids, lies beneath the resin surface. | Contamination can weaken adhesion, cure, and chemical resistance. | Material, dimensions, depth, affected interface, and whether a structural or barrier bond is interrupted. | Remove contaminated laminate and rebuild the area where qualified criteria require correction. |  |  |  | Fiberglass tank relining | https://www.plastechservices.com/fiberglass-tank-reline | Open | Open visualizer
80 | I27 | Internal | Laminate and fabrication | Improper cure and abnormal Barcol hardness | Softness, uneven gloss, amber discoloration, impressions, burn marks, shrink cracks, voids, or delamination indicate abnormal cure. | Chemical resistance and structural properties may be inadequate. | Hardness pattern, affected depth and area, resin condition, service exposure, and related defects. | Remove and rebuild unsound undercured or exotherm-damaged laminate unless a qualified material evaluation supports another disposition. |  |  |  | Fiberglass tank relining | https://www.plastechservices.com/fiberglass-tank-reline | Open | Open visualizer
81 | I28 | Internal | Laminate and fabrication | Uneven corrosion-barrier or structural thickness | The liner tapers abnormally, veil is missing, or structural plies are locally thin. | Chemical life and structural capacity can both be reduced. | Actual barrier and wall thickness, missing plies, affected area, design loads, and service exposure. | Restore the barrier and add engineered structural reinforcement where supported by the design basis; widespread deficiency may require replacement. |  |  |  | Fiberglass tank relining | https://www.plastechservices.com/fiberglass-tank-reline | Open | Open visualizer
82 | I29 | Internal | Internal connections and hardware | Internal nozzle chemical attack | The nozzle bore, flange face, neck, or transition becomes rough, discolored, pitted, or veil-exposed. | Nozzle geometry concentrates both process exposure and external piping load. | Damage depth, remaining wall, bond condition, flow pattern, chemistry, and external loads. | Rebuild the compatible nozzle liner or replace the nozzle and transition where deterioration is too deep or extensive. |  |  |  | FRP tank nozzle and flange repair | https://www.plastechservices.com/fiberglass-tank-nozzle-repair | Open | Open visualizer
83 | I30 | Internal | Internal connections and hardware | Nozzle-to-shell internal bond cracking | A crescent crack and radial branches form at the internal nozzle fillet or secondary bond. | Cracking can compromise the liner, bond, and containment path. | Depth, circumference, bond integrity, external pipe loads, and surrounding shell condition. | Correct connection loads and rebuild the bond or nozzle under a qualified repair design. |  |  |  | FRP tank nozzle and flange repair | https://www.plastechservices.com/fiberglass-tank-nozzle-repair | Open | Open visualizer
84 | I31 | Internal | Internal connections and hardware | Internal nozzle or manway delamination | The neck, repad, transition, or field laminate lifts or separates between plies or from the parent wall. | The penetration may lose structural continuity and barrier protection. | Interface, extent, substrate condition, load path, and related cracking. | Remove and rebuild the affected secondary laminate or replace the connection when the parent structure cannot support repair. |  |  |  | FRP tank nozzle and flange repair | https://www.plastechservices.com/fiberglass-tank-nozzle-repair | Open | Open visualizer
85 | I32 | Internal | Internal connections and hardware | Manway internal-surface degradation | Scuffing, rough edge sealing, chemical staining, chips, or transition cracking affects the manway interior. | Damage occurs at a large opening and may extend beneath the cover or into the shell bond. | Neck and flange condition, edge sealing, crack depth, bond integrity, and access-related damage. | Restore compatible sealing and laminate or rebuild the manway connection where required. |  |  |  | FRP tank nozzle and flange repair | https://www.plastechservices.com/fiberglass-tank-nozzle-repair | Open | Open visualizer
86 | I33 | Internal | Internal connections and hardware | Internal hardware, baffle, or mixer abrasion and impact | Rub tracks, impact marks, whitening, or cracking aligns with a loose or moving internal component. | Repeated contact can damage both the hardware attachment and tank wall or bottom. | Hardware stability, contact path, attachment bond, wall damage, and cyclic loading. | Secure, modify, or replace the responsible component and reconstruct affected tank laminate under qualified design. |  |  |  | Fiberglass tank relining | https://www.plastechservices.com/fiberglass-tank-reline | Open | Open visualizer
87 | I34 | Internal | Structural damage and material change | Radial, axial, circumferential, or helical structural cracks | Larger cracks follow load paths around penetrations, transitions, supports, or principal shell stresses. | Orientation can signal structural involvement beyond the inner liner. | Direction, depth, length, fiber breakage, delamination, growth, and initiating load. | Correct the load and perform engineered structural reconstruction or replace the affected section where remaining laminate is insufficient. |  |  |  | Fiberglass tank relining | https://www.plastechservices.com/fiberglass-tank-reline | Open | Open visualizer
88 | I35 | Internal | Structural damage and material change | Fiber fracture | Broken glass bundles cross a crack or damaged zone rather than remaining continuous. | Reinforcement capacity has been directly lost. | Fracture area, ply orientations, remaining wall, connected delamination, and load history. | An engineered structural rebuild may be possible when localized; extensive fiber fracture generally favors component or tank replacement. |  |  |  | Fiberglass tank relining | https://www.plastechservices.com/fiberglass-tank-reline | Open | Open visualizer
89 | I36 | Internal | Structural damage and material change | Wall thinning and structural-laminate loss | A broad internal depression shows loss beyond the corrosion barrier into structural plies. | Effective load-carrying wall thickness is reduced. | Remaining thickness, full area, fiber condition, design loads, and active deterioration source. | Restore structure and barrier under an engineered repair or reline design when localized; widespread wall loss may require replacement. |  |  |  | Fiberglass tank relining | https://www.plastechservices.com/fiberglass-tank-reline | Open | Open visualizer
90 | I37 | Internal | Structural damage and material change | Swelling, softening, embrittlement, or dimensional change | Resin becomes swollen and soft or dry, brittle, and shrink-cracked, with local dimensional change. | Changed material properties create secondary stress and uncertain remaining performance. | Affected depth and area, chemical and temperature history, fiber condition, and structural involvement. | Remove altered laminate and rebuild or reline if bounded; deep or widespread material change may require replacement. |  |  |  | Fiberglass tank relining | https://www.plastechservices.com/fiberglass-tank-reline | Open | Open visualizer
91 | I38 | Internal | Structural damage and material change | Thermal-shock or thermal-fatigue cracking | Closely spaced cracks develop along a temperature-transition zone, often progressing from hairlines to a longer crack. | Thermal cycling can damage the liner, resin, bonds, and laminate interfaces. | Temperature history, crack depth, interface damage, affected area, and continuing operating cycle. | Correct the thermal transition and rebuild damaged barrier or laminate under a qualified repair design. |  |  |  | Fiberglass tank relining | https://www.plastechservices.com/fiberglass-tank-reline | Open | Open visualizer
92 | I39 | Internal | Structural damage and material change | Mechanical fatigue cracking | Multiple progressively sized cracks and a possible delamination halo appear at a cyclic stress location. | Damage may continue growing even when no single overload occurred. | Cycle history, crack growth, delamination, fiber condition, and load source. | Eliminate or reduce the cyclic load and perform engineered repair or replacement based on remaining laminate. |  |  |  | Fiberglass tank relining | https://www.plastechservices.com/fiberglass-tank-reline | Open | Open visualizer
93 | I40 | Internal | Laminate and fabrication | Internal repair or reline failure | A newer patch, coating, or liner blisters, cracks, lifts, peels, disbonds, or leaks. | The repair can conceal continuing attack or transfer damage to adjacent laminate. | Original failure, substrate soundness, bond extent, compatibility, cure, and service exposure. | Remove the failed system, reassess the substrate, and redesign the repair or reline—or replace the tank—using qualified materials and engineering. |  |  |  | Fiberglass tank relining | https://www.plastechservices.com/fiberglass-tank-reline | Open | Open visualizer
94 | I41 | Internal | Containment and catastrophic failure | Through-wall crack and seepage | An internal crack crosses the complete wall and appears externally as a damp spot or slow weep. | Both barrier and structural containment have been breached. | Safe isolation, crack and wetting extent, surrounding wall, root cause, and remaining capacity. | Keep the tank out of service until an engineered repair, reline, major reconstruction, or replacement is selected. |  |  |  | Fiberglass tank relining | https://www.plastechservices.com/fiberglass-tank-reline | Open | Open visualizer
95 | I42 | Internal | Containment and catastrophic failure | Through-wall leakage | A continuous liquid stream passes through a degraded or cracked lower-shell or bottom area. | Active containment loss can enlarge and expose surrounding equipment and personnel. | Leak path, total degraded area, chemical exposure, structural wall condition, and event progression. | Isolate and make safe; repair only under an engineered scope, with relining or replacement considered where deterioration is extensive. |  |  |  | Fiberglass tank relining | https://www.plastechservices.com/fiberglass-tank-reline | Open | Open visualizer
96 | I43 | Internal | Containment and catastrophic failure | Spray or jet leakage | Liquid head or pressure drives a narrow energetic release through a hole or crack. | The release indicates a complete containment breach and may be hazardous at a distance. | Safe isolation, pressure or liquid head, opening geometry, surrounding damage, and root cause. | Keep the tank out of service; select engineered reconstruction or replacement only after full damage assessment. |  |  |  | Fiberglass tank relining | https://www.plastechservices.com/fiberglass-tank-reline | Open | Open visualizer
97 | I44 | Internal | Containment and catastrophic failure | Overpressure rupture | Outward bulging, stretched laminate, radial cracking, or a developing split follows excessive internal pressure. | The load may have exceeded the intended capability of the whole tank. | Pressure event, venting, shell and roof deformation, fiber damage, and global geometry. | Correct the pressure and venting cause; extensive rupture generally requires replacement, while any reconstruction needs a complete engineering basis. |  |  |  | Fiberglass tank relining | https://www.plastechservices.com/fiberglass-tank-reline | Open | Open visualizer
98 | I45 | Internal | Containment and catastrophic failure | Vacuum collapse | The shell or roof pulls inward with compressed liner wrinkles and buckle ridges. | Global instability can damage multiple plies, nozzles, roof, and shell geometry. | Venting event, full deformation, cracking, delamination, and remaining structural shape. | Correct the vacuum cause and obtain engineered disposition; major collapse commonly points toward large reconstruction or replacement. |  |  |  | Fiberglass tank relining | https://www.plastechservices.com/fiberglass-tank-reline | Open | Open visualizer
99 | I46 | Internal | Containment and catastrophic failure | Catastrophic bottom or shell rupture | A large opening with peeled laminate layers, broken glass bundles, and separated corrosion barrier causes a major release. | Primary containment and structural continuity are lost. | Event cause, complete tank and foundation damage, connections, and whether any material remains reusable. | Replacement is generally the primary consideration; exceptional reconstruction requires comprehensive qualified engineering. |  |  |  | Fiberglass tank relining | https://www.plastechservices.com/fiberglass-tank-reline | Open | Open visualizer

## Photo Log
PHOTOGRAPH AND MEDIA LOG
Create a sequence of overall, medium, and close views. Preserve the original file and record annotations separately.
Suggested file name: TK101_2026-07-26_EXT_N3_03OCLOCK_DETAIL_001.jpg
Photo ID | File name | Date | Time | Photographer | Tank ID | Scope | Component | Precise location | View | Direction | Condition ID | Scale included | Observation record | Caption | Notes
P001
P002
P003
P004
P005
P006
P007
P008
P009
P010
P011
P012
P013
P014
P015
P016
P017
P018
P019
P020
P021
P022
P023
P024
P025
P026
P027
P028
P029
P030
P031
P032
P033
P034
P035
P036
P037
P038
P039
P040

## Observation Register
OBSERVATION REGISTER
Create a traceable record for each visible condition. This register does not assign a structural rating or fitness-for-service decision.
Metric | Value | Metric | Value | Metric | Value | Metric | Value
Records entered | 50 | Observed | 0 | Prompt evaluation | 0 | Emergency procedure | 0
Record | Date | Observer | Condition and precise location | Condition ID | Observation status | What is visible and extent | Surface state | Photo IDs | Comparison / immediate action | Follow-up status | Responsible party | Target / review date
OBS-001
OBS-002
OBS-003
OBS-004
OBS-005
OBS-006
OBS-007
OBS-008
OBS-009
OBS-010
OBS-011
OBS-012
OBS-013
OBS-014
OBS-015
OBS-016
OBS-017
OBS-018
OBS-019
OBS-020
OBS-021
OBS-022
OBS-023
OBS-024
OBS-025
OBS-026
OBS-027
OBS-028
OBS-029
OBS-030
OBS-031
OBS-032
OBS-033
OBS-034
OBS-035
OBS-036
OBS-037
OBS-038
OBS-039
OBS-040
OBS-041
OBS-042
OBS-043
OBS-044
OBS-045
OBS-046
OBS-047
OBS-048
OBS-049
OBS-050

## AST Supplement
ABOVEGROUND STORAGE TANK SUPPLEMENT
Document foundation, supports, weather exposure, connections, attachments, secondary containment, and prior work from repeatable viewpoints.
Status | Focused item | Location / record reference | Photo IDs | Follow-up status | Notes
Not observed | Foundation settlement, cracking, drainage, and support continuity |  |  | Documented for record
Not observed | Bottom-edge and lower-knuckle condition |  |  | Documented for record
Not observed | Shell plumbness, roundness, bulging, or buckling |  |  | Documented for record
Not observed | Anchor lugs, hold-downs, saddles, skirts, and metallic hardware |  |  | Documented for record
Not observed | UV exposure, weathering, exterior resin condition, and fiber blooming |  |  | Documented for record
Not observed | Nozzle loading from piping, valves, equipment, and thermal movement |  |  | Documented for record
Not observed | Roof, vent, overflow, mixer, ladder, platform, and handrail attachments |  |  | Documented for record
Not observed | Secondary containment staining, standing liquid, and drainage |  |  | Documented for record
Not observed | Flood, uplift, wind, freeze, fire, heat, or seismic history |  |  | Documented for record
Not observed | Prior repairs, overlaminates, and recurring locations |  |  | Documented for record
Relevant Plastech service: Fiberglass tank repair ¦ (410) 737-4700 |  |  |  |  | Open service page

## UST Supplement
UNDERGROUND STORAGE TANK SUPPLEMENT
Document accessible components and available records without assuming the condition of buried or otherwise inaccessible surfaces.
Status | Focused item | Location / record reference | Photo IDs | Follow-up status | Notes
Not observed | Accessible risers, sumps, vaults, covers, and penetrations |  |  | Documented for record
Not observed | Fill, vent, withdrawal, and monitoring connections |  |  | Documented for record
Not observed | Settlement, movement, loading, or damage at accessible piping |  |  | Documented for record
Not observed | Groundwater, flood, uplift, or flotation history |  |  | Documented for record
Not observed | Leak-detection or monitoring records |  |  | Documented for record
Not observed | Product inventory or reconciliation concerns |  |  | Documented for record
Not observed | Access or excavation history |  |  | Documented for record
Not observed | Prior lining, relining, patching, or nozzle work |  |  | Documented for record
Not observed | Available installation, backfill, anchorage, and test records |  |  | Documented for record
Not observed | Buried or inaccessible surfaces identified as not accessible |  |  | Documented for record
Relevant Plastech service: Underground tank repair and relining ¦ (410) 737-4700 |  |  |  |  | Open service page

## Tanker Supplement
FRP TANKER TRAILER SUPPLEMENT
Document chemical service together with cyclic road loading, vibration, impact exposure, equipment connections, and prior repair history.
Status | Focused item | Location / record reference | Photo IDs | Follow-up status | Notes
Not observed | Overall shell shape and exterior laminate |  |  | Documented for record
Not observed | Impact, abrasion, gouging, stress whitening, and exposed fibers |  |  | Documented for record
Not observed | Saddles, frame interfaces, supports, and attachment points |  |  | Documented for record
Not observed | Manways, hatches, gaskets, covers, and fasteners |  |  | Documented for record
Not observed | Inlets, outlets, valves, vents, hoses, and connected piping |  |  | Documented for record
Not observed | Baffles and internal attachments, when inspection is authorized |  |  | Documented for record
Not observed | Road-debris, tire, jackknife, rollover, and collision damage |  |  | Documented for record
Not observed | UV and weather exposure |  |  | Documented for record
Not observed | Cargo compatibility, cleaning history, and temperature history |  |  | Documented for record
Not observed | Prior repairs and recurring conditions |  |  | Documented for record
Relevant Plastech service: Fiberglass tank repair ¦ (410) 737-4700 |  |  |  |  | Open service page

## Repair Readiness
REPAIR-READINESS RECORD
Prepare the asset, service, condition, load, access, schedule, and documentation information needed for qualified evaluation and scope development.
Status | Information for scope development | Source / owner | Reference | Provided date | Notes
Not started | Tank identification and drawings
Not started | Manufacturer and laminate information
Not started | Current and historical product
Not started | Chemical concentration and contaminants
Not started | Operating and design temperatures
Not started | Operating and design pressure or vacuum
Not started | Specific gravity and liquid level
Not started | Agitation, flow, solids, abrasion, and impingement
Not started | Venting and overflow configuration
Not started | Condition map and observation records
Not started | Original, unedited photographs
Not started | Measurements and test records produced by qualified personnel
Not started | Prior inspection, repair, and reline records
Not started | Connected piping, valve, equipment, and thermal-movement information
Not started | Foundation, anchorage, support, and settlement information
Not started | Facility-controlled access, cleaning, and site-work requirements
Not started | Required quality records and acceptance basis
Not started | Required project schedule and outage window

## Plastech Services
PLASTECH SERVICES AND CONTACT DIRECTORY
Plastech Services, Inc. ¦ (410) 737-4700 ¦ www.plastechservices.com
Share tank drawings, service conditions, operating history, photographs, and inspection records. Choose the service that matches the asset and question. For an urgent condition, follow the facility's emergency and site-control procedures first; then contact Plastech when site controls are active.
Need | Customer-facing service | Destination | Open | How to use the link
Company information | Visit Plastech Services | https://www.plastechservices.com/ | Open page | Company, capabilities, and current contact information
Inspection planning | Fiberglass tank inspection | https://www.plastechservices.com/fiberglass-tank-inspection | Open page | Condition assessment, documentation, and repair planning
99-condition companion | FRP Tank Failure Visualizer | https://www.plastechservices.com/frp-tank-failure-visualizer | Open page | Educational visual reference
General tank damage | Fiberglass tank repair | https://www.plastechservices.com/fiberglass-tank-repair | Open page | External cracks, leaks, impact, supports, shell, roof, and bottom damage
Internal deterioration | Fiberglass tank relining | https://www.plastechservices.com/fiberglass-tank-reline | Open page | Widespread blistering, chemical attack, and corrosion-barrier deterioration
Connections and openings | FRP tank nozzle and flange repair | https://www.plastechservices.com/fiberglass-tank-nozzle-repair | Open page | Nozzles, flanges, manways, vents, drains, fittings, and pipe-loading damage
Underground tanks | Underground tank repair and relining | https://www.plastechservices.com/underground-storage-tank-repair-reline | Open page | UST repair, relining, modification, penetrations, ribs, and accessible areas
Field-executed work | Onsite FRP services | https://www.plastechservices.com/onsite-frp-fiberglass-services | Open page | Onsite evaluation, repair, modification, reinforcement, or installation
Connected piping | Fiberglass pipe repair | https://www.plastechservices.com/fiberglass-pipe-repair | Open page | FRP piping, joints, fittings, and connected-system issues
Urgent response | Emergency response services | https://www.plastechservices.com/emergency-response-services | Open page | After facility emergency and site-control procedures are active
Project review | Request a project review | https://www.plastechservices.com/quote | Open page | Submit project details and supporting records
Chemical processing | Chemical-processing maintenance services | https://www.plastechservices.com/industries/chemical-processing | Open page | Industry-specific service information
Pulp and paper | Pulp and paper facility services | https://www.plastechservices.com/industries/pulp-and-paper-mill | Open page | Industry-specific service information
Water and wastewater | Water and wastewater infrastructure services | https://www.plastechservices.com/industries/wastewater-treatment | Open page | Industry-specific service information
COMPANY QUALIFICATION NOTE Plastech Services, Inc. is an ISO 9001-certified company. The certification applies to the organization's quality-management system, not to an individual repair, reline, material, or field result. Project-specific safety, confined-space, insurance, facility, and scope requirements must still be confirmed.